## SV attacks
Attack condition | FDI Type | Label | Attack Targets | No. of datasets | Sub-scenario ID | Descriptions | Possible physical impacts | Untrusted Mus | Malicious Program ID | Time sections of successive behaviours in seconds
When short-circuit faults happen, compromised MUs spoof fault-free situations to disable safety protection | Add | 911 | MU1 (66kV) | 2 | 9111a-9111b | (9111, 9121, 9131, 9141) Inject messages every 50ms (normal HeartBeat is 50ms) with counterfeit measurements to fake fault-free situations only when an over-current status occurs (measurements exceed the pre-defined threshold). The malware stops injecting when the actual measurements are back to normal. | Circuit breakers STILL trip and the safety protection is STILL functional | MU1 | 9111 | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total | The DMZ represents a buffer between the 1st attack cycle and the 2nd attack cycle. Since systems were recovered from a real/fabricated fault, the data in DMZ was labelled as 0.
|  | 912 | MU1 (XFMR) | 2 | 9121a-9121b |  |  |  |  | 20 | 5 | 35 | 10 | 20 | 5 | 25 | 120
|  | 913 | MU2 (22kV) | 2 | 9131a-9131b |  |  | MU2 | 9131
|  | 914 | MU2 (FDR) | 4 | 9141a-9141d
|  | 911 | MU1 (66kV) | 2 | 9112a-9112b | (9112, 9122, 9132, 9142) Inject messages every 25ms (normal HeartBeat is 50ms) with counterfeit measurements to fake fault-free situations only when an over-current status occurs (measurements exceed the pre-defined threshold). The malware stops injecting when the actual measurements are back to normal. | Circuit breakers STILL trip and the safety protection is STILL functional | MU1 | 9112 | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 912 | MU1 (XFMR) | 2 | 9122a-9122b |  |  |  |  | 20 | 5 | 35 | 10 | 20 | 5 | 25 | 120
|  | 913 | MU2 (22kV) | 2 | 9132a-9132b |  |  | MU2 | 9132
|  | 914 | MU2 (FDR) | 4 | 9142a-9142d
| Alter | 921 | MU1 (66kV) | 2 | 921a-921b | (921, 922, 923, 924) Alter original messages with counterfeit measurements to fake fault-free situations even when an over-current status occurs (measurements exceed the pre-defined threshold). The malware stops injecting when the actual measurements are back to normal. | Circuit breakers NEVER trip and the safety protection ALWAYS failed | MU1 | 921 | Fault-free | Attacks | Fault-free | DMZ | Fault-free | Attacks | Total
|  | 922 | MU1 (XFMR) | 2 | 922a-922b |  |  |  |  | 20 | 30 | 10 | 10 | 20 | 30 | 120
|  | 923 | MU2 (22kV) | 2 | 923a-923b |  |  | MU2 | 923
|  | 924 | MU2 (FDR) | 4 | 924a-924d
In fault-free operations, compromised MUs spoof one of the ten emergency situations without following the KCL/KVL laws. | Add | 931 | MU1 (66kV) | 2 | 9311a-9311b | Inject 100 packets with 50ms HB to spoof one of the ten emergency situations: 9311a: 66kV1=F_66kV1=2017; 9311b: 66kV3=F_66kV2=2017; 9321a: 66kV1=XFMR1W1=XFMR1W2=CB_XFMR1=F_XFMR1=2017; 9321b: 66kV3=XFMR2W1=XFMR2W2=CB_XFMR2=F_XFMR2=2017; 9323a: 66kV1=XFMR1W1=1000, XFMR1W2=1732, CB_XFMR1=0, F_XFMR1=3000; 9323b: 66kV3=XFMR2W1=1000, XFMR2W2=1732, CB_XFMR2=0, F_XFMR2=3000; 9331a: 22kV1=F_22kV1=2017; 9331b: 22kV3=F_22kV2=2017; 9341a: FDR1=22kV1=F_FDR1=2017; 9341b: FDR2=F_FDR2=2017; 9341c: FDR3=F_FDR3=2017; 9341d: FDR4=22kV3=F_FDR4=2017. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9311a-9311b | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 932 | MU1 (XFMR) | 2 | 9321a-9321b |  |  |  | 9321a-9321b | 15 | 5 | 15 | 10 | 15 | 5 | 15 | 10 | 15 | 5 | 10 | 120
|  |  |  | 2 | 9323a-9323b |  |  |  | 9323a-9323b
|  | 933 | MU2 (22kV) | 2 | 9331a-9331b |  |  | MU2 | 9331a-9331b
|  | 934 | MU2 (FDR) | 4 | 9341a-9341d |  |  |  | 9341a-9341d
|  | 931 | MU1 (66kV) | 2 | 9312a-9312b | Inject 80 packets with 25ms HB to spoof one of the ten emergency situations: 9312a: 66kV1=F_66kV1=2017; 9312b: 66kV3=F_66kV2=2017; 9322a: 66kV1=XFMR1W1=XFMR1W2=CB_XFMR1=F_XFMR1=2017; 9322b: 66kV3=XFMR2W1=XFMR2W2=CB_XFMR2=F_XFMR2=2017; 9324a: 66kV1=XFMR1W1=1000, XFMR1W2=1732, CB_XFMR1=0, F_XFMR1=3000; 9324b: 66kV3=XFMR2W1=1000, XFMR2W2=1732, CB_XFMR2=0, F_XFMR2=3000; 9332a: 22kV1=F_22kV1=2017; 9332b: 22kV3=F_22kV2=2017; 9342a: FDR1=22kV1=F_FDR1=2017; 9342b: FDR2=F_FDR2=2017; 9342c: FDR3=F_FDR3=2017; 9342d: FDR4=22kV3=F_FDR4=2017. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9312a-9312b | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 932 | MU1 (XFMR) | 2 | 9322a-9322b |  |  |  | 9322a-9322b | 15 | 2 | 18 | 10 | 15 | 2 | 18 | 10 | 15 | 2 | 13 | 120
|  |  |  | 2 | 9324a-9324b |  |  |  | 9324a-9324b
|  | 933 | MU2 (22kV) | 2 | 9332a-9332b |  |  | MU2 | 9332a-9332b
|  | 934 | MU2 (FDR) | 4 | 9342a-9342d |  |  |  | 9342a-9342d
| Alter | 941 | MU1 (66kV) | 2 | 9411a-9411b | Modify the measurements of 20 packets to spoof one of the ten emergency situations: 9411a: 66kV1=F_66kV1=2017; 9411b: 66kV3=F_66kV2=2017; 9421a: 66kV1=XFMR1W1=XFMR1W2=CB_XFMR1=F_XFMR1=2017; 9421b: 66kV3=XFMR2W1=XFMR2W2=CB_XFMR2=F_XFMR2=2017; 9423a: 66kV1=XFMR1W1=1000, XFMR1W2=1732, CB_XFMR1=0, F_XFMR1=3000; 9423b: 66kV3=XFMR2W1=1000, XFMR2W2=1732, CB_XFMR2=0, F_XFMR2=3000; 9431a: 22kV1=F_22kV1=2017; 9431b: 22kV3=F_22kV2=2017; 9441a: FDR1=22kV1=F_FDR1=2017; 9441b: FDR2=F_FDR2=2017; 9441c: FDR3=F_FDR3=2017; 9441d: FDR4=22kV3=F_FDR4=2017. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9411a-9411b | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 942 | MU1 (XFMR) | 2 | 9421a-9421b |  |  |  | 9421a-9421b | 15 | 1 | 19 | 10 | 15 | 1 | 19 | 10 | 15 | 1 | 14 | 120
|  |  |  | 2 | 9423a-9423b |  |  |  | 9423a-9423b
|  | 943 | MU2 (22kV) | 2 | 9431a-9431b |  |  | MU2 | 9431a-9431b
|  | 944 | MU2 (FDR) | 4 | 9441a-9441d |  |  |  | 9441a-9441d
|  | 941 | MU1 (66kV) | 2 | 9412a-9412b | Modify the measurements of 2 packets to spoof one of the ten emergency situations: 9412a: 66kV1=F_66kV1=2017; 9412b: 66kV3=F_66kV2=2017; 9422a: 66kV1=XFMR1W1=XFMR1W2=CB_XFMR1=F_XFMR1=2017; 9422b: 66kV3=XFMR2W1=XFMR2W2=CB_XFMR2=F_XFMR2=2017; 9424a: 66kV1=XFMR1W1=1000, XFMR1W2=1732, CB_XFMR1=0, F_XFMR1=3000; 9424b: 66kV3=XFMR2W1=1000, XFMR2W2=1732, CB_XFMR2=0, F_XFMR2=3000; 9432a: 22kV1=F_22kV1=2017; 9432b: 22kV3=F_22kV2=2017; 9442a: FDR1=22kV1=F_FDR1=2017; 9442b: FDR2=F_FDR2=2017; 9442c: FDR3=F_FDR3=2017; 9442d: FDR4=22kV3=F_FDR4=2017. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9412a-9412b | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 942 | MU1 (XFMR) | 2 | 9422a-9422b |  |  |  | 9422a-9422b | 15 | 0.1 | 19.9 | 10 | 15 | 0.1 | 19.9 | 10 | 15 | 0.1 | 14.9 | 120
|  |  |  | 2 | 9424a-9424b |  |  |  | 9424a-9424b
|  | 943 | MU2 (22kV) | 2 | 9432a-9432b |  |  | MU2 | 9432a-9432b
|  | 944 | MU2 (FDR) | 4 | 9442a-9442d |  |  |  | 9442a-9442d
In fault-free operations, compromised MUs spoof one of the ten emergency scenarios by replaying the recorded measurements from a previous faulty situation. | Add | 951 | MU1 (66kV) | 2 | 9511a-9511b | Inject all recorded packets with 50ms HB to spoof one of the ten emergency situations. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9511 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 952 | MU1 (XFMR) | 2 | 9521a-9521b |  |  |  | 9521 | 20 | 70 | 30 | 3 | 27 | 10 | 20 | 3 | 17 | 200
|  | 953 | MU2 (22kV) | 2 | 9531a-9531b |  |  | MU2 | 9531
|  | 954 | MU2 (FDR) | 4 | 9541a-9541d |  |  |  | 9541
|  | 951 | MU1 (66kV) | 2 | 9512a-9512b | Inject all recorded packets with 25ms HB to spoof one of the ten emergency situations. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9512 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 952 | MU1 (XFMR) | 2 | 9522a-9522b |  |  |  | 9522 | 20 | 70 | 30 | 1.5 | 28.5 | 10 | 20 | 1.5 | 18.5 | 200
|  | 953 | MU2 (22kV) | 2 | 9532a-9532b |  |  | MU2 | 9532
|  | 954 | MU2 (FDR) | 4 | 9542a-9542d |  |  |  | 9542
|  | 951 | MU1 (66kV) | 2 | 9513a-9513b | Inject the first half of the recorded packets with 25ms HB to spoof one of the ten emergency situations. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9513 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 952 | MU1 (XFMR) | 2 | 9523a-9523b |  |  |  | 9523 | 20 | 70 | 30 | 0.75 | 29.25 | 10 | 20 | 0.75 | 19.25 | 200
|  | 953 | MU2 (22kV) | 2 | 9533a-9533b |  |  | MU2 | 9533
|  | 954 | MU2 (FDR) | 4 | 9543a-9543d |  |  |  | 9543
| Alter | 961 | MU1 (66kV) | 2 | 9611a-9611b | Modify the measurements of original SV packets based on all the recorded measurements from a previous emergency scenario. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9611 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 962 | MU1 (XFMR) | 2 | 9621a-9621b |  |  |  | 9621 | 20 | 70 | 30 | 3 | 27 | 10 | 20 | 3 | 17 | 200
|  | 963 | MU2 (22kV) | 2 | 9631a-9631b |  |  | MU2 | 9631
|  | 964 | MU2 (FDR) | 4 | 9641a-9641d |  |  |  | 9641
|  | 961 | MU1 (66kV) | 2 | 9612a-9612b | Modify the measurements of original SV packets based on the first 1/3 of the recorded measurements from a previous emergency scenario. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9612 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 962 | MU1 (XFMR) | 2 | 9622a-9622b |  |  |  | 9622 | 20 | 70 | 30 | 1 | 29 | 10 | 20 | 1 | 19 | 200
|  | 963 | MU2 (22kV) | 2 | 9632a-9632b |  |  | MU2 | 9632
|  | 964 | MU2 (FDR) | 4 | 9642a-9642d |  |  |  | 9642
|  | 961 | MU1 (66kV) | 2 | 9613a-9613b | Modify the measurements of original SV packets based on all the recorded measurements from a previous emergency scenario, while increasing the measurement values to 1.1 times. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9613 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 962 | MU1 (XFMR) | 2 | 9623a-9623b |  |  |  | 9623 | 20 | 70 | 30 | 3 | 27 | 10 | 20 | 3 | 17 | 200
|  | 963 | MU2 (22kV) | 2 | 9633a-9633b |  |  | MU2 | 9633
|  | 964 | MU2 (FDR) | 4 | 9643a-9643d |  |  |  | 9643
|  | 961 | MU1 (66kV) | 2 | 9614a-9614b | Modify the measurements of original SV packets based on the first 1/4 of the recorded measurements from a previous emergency scenario, while increasing the measurement values to 1.2 times. | Circuit breakers ALWAYS trip while the power supply is ALWAYS interrupted. | MU1 | 9614 | Fault-free | Emergency | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 962 | MU1 (XFMR) | 2 | 9624a-9624b |  |  |  | 9624 | 20 | 70 | 30 | 0.75 | 29.25 | 10 | 20 | 0.75 | 19.25 | 200
|  | 963 | MU2 (22kV) | 2 | 9634a-9634b |  |  | MU2 | 9634
|  | 964 | MU2 (FDR) | 4 | 9644a-9644d |  |  |  | 9644
Total Datasets (with labels) |  |  |  | 148
When short-circuit faults happen, compromised MUs delete SV packets | Delete | 971 | MU1 (66kV) | 2 | 971a-971b | Delete the first 100 SV packets when a fault occurs. Thus, delay protection for almost 5 seconds (100*50ms=5s). | Circuit breakers trip with a 5-second DELAY and the safety protection DELAY for 5 seconds. | MU1 | 971 | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 972 | MU1 (XFMR) | 2 | 972a-972b |  |  |  |  | 20 | 5 | 75 | 10 | 20 | 5 | 25 | 160
|  | 973 | MU2 (22kV) | 2 | 973a-973b |  |  | MU2 | 973
|  | 974 | MU2 (FDR) | 4 | 974a-974d
Additional Datasets (without labels) |  |  |  | 10

## Benign-behaviour-only
Scenario type | Label | No. of datasets | Descriptions | Time sections of successive behaviours in seconds |  |  |  | Total
Fault-free | 0 | 1 | No unusual events happen. | All fault-free |  |  |  | 270
|  |  |  | Fault-free | Emergency | Fault-free (recovery) | Emergency
Emergency operation | 101 | 1 | When a short-circuit fault occurs on Fault_66bus1, open CB1_66KV, CB2_66KV and CB_XFMR1; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 102 | 1 | When a short-circuit fault occurs on Fault_66bus2, open CB2_66KV, CB3_66KV and CB_XFMR2; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 103 | 1 | When a short-circuit fault occurs on Fault_XFMR1, open CB1_66KV, CB2_66KV and CB_XFMR1; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 104 | 1 | When a short-circuit fault occurs on Fault_XFMR2, open CB2_66KV, CB3_66KV and CB_XFMR2; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 105 | 1 | When a short-circuit fault occurs on Fault_22bus1, open CB1_22KV | 30 | 90 | 60 | 90 | 270
| 106 | 1 | When a short-circuit fault occurs on Fault_22bus2, open CB3_22KV | 30 | 90 | 60 | 90 | 270
| 107 | 1 | When a short-circuit fault occurs on Fault_FDR1, open CB_FDR1 | 30 | 90 | 60 | 90 | 270
| 108 | 1 | When a short-circuit fault occurs on Fault_FDR2, open CB_FDR2 | 30 | 90 | 60 | 90 | 270
| 109 | 1 | When a short-circuit fault occurs on Fault_FDR3, open CB_FDR3 | 30 | 90 | 60 | 90 | 270
| 110 | 1 | When a short-circuit fault occurs on Fault_FDR4, open CB_FDR4 | 30 | 90 | 60 | 90 | 270