## SV attacks
Attack condition | FDI Type | Label | Attack Targets | No. of datasets | Sub-scenario ID | Descriptions | Possible physical impacts | Untrusted Mus | Malicious Program ID |  | Time sections of successive behaviours in seconds
When a phase-to-phase fault happens (emergency situation) | Add | 911 | MU1 (66kV) | 2 | 9111a-9111b | (9111, 9121, 9131, 9141) Inject additional messages with 50ms HB (normal HB is 50ms) to fake normal situations only when an over-current status occurs (stop injecting when the fault is isolated). | Circuit breakers still tripped and the fault is isolated | MU1 | 9111 | need to create | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 912 | MU1 (XFMR) | 2 | 9121a-9121b | [5 empty] | 20 | 5 | 35 | 20 | 20 | 5 | 35 | 140
|  | 913 | MU2 (22kV) | 2 | 9131a-9131b |  |  | MU2 | 9131
|  | 914 | MU2 (FDR) | 4 | 9141a-9141d
|  | 911 | MU1 (66kV) | 2 | 9112a-9112b | (9112, 9122, 9132, 9142) Inject additional messages with 25ms HB (normal HB is 50ms) to fake normal situation only when an over-current status occurs (stop injecting when the fault is isolated). | Circuit breakers still tripped and the fault is isolated | MU1 | 9112 | previous 911 | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 912 | MU1 (XFMR) | 2 | 9122a-9122b | [5 empty] | 20 | 5 | 35 | 20 | 20 | 5 | 35 | 140
|  | 913 | MU2 (22kV) | 2 | 9132a-9132b |  |  | MU2 | 9132 | previous 912
|  | 914 | MU2 (FDR) | 4 | 9142a-9142d
| Alter | 921 | MU1 (66kV) | 2 | 921a-921b | (921, 922, 923, 924) Alter original messages to fake normal situations even when an over-current status occurs. | Protection mechanism fails | MU1 | 921 | previous 913 | Fault-free | Attacks | Emergency | DMZ | Fault-free | Attacks | Emergency | Total
|  | 922 | MU1 (XFMR) | 2 | 922a-922b | [5 empty] | 20 | 30 | ? | ? | ? | ? | ? | 50
|  | 923 | MU2 (22kV) | 2 | 923a-923b |  |  | MU2 | 923 | previous 914
|  | 924 | MU2 (FDR) | 4 | 924a-924d
[14 empty] | DMZ | The DMZ represents a buffer between the 1st attack cycle and the 2nd attack cycle. Two different colours of DMZ indicate two different statuses.
When short-circuit faults happen, mislead associated CBs with fake closing signals to disable safety protection | Add | 831 | IED_XFMR1 (66kV) | 1 | 8311a | (8311, 8321, 8331) Inject messages (500ms HB) to mislead associated CBs with fake closing signals |  | IED_PIOC_XFMR1 | 8311 |  | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total | DMZ | means outliers (non valid data) because MATLAB cannot process the physical behaviours of such attacks reasonably (transformers will be damaged physically in the real world). Data was labelled as N/V.
|  |  | IED_XFMR1 (XFMR) | 1 | 8311b | [5 empty] | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8311c |  |  | IED_PIOC_XFMR2 | 8311 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8311d | [8 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8321a-8321b |  |  | IED_PIOC_FDR | 8321 |  |  |  |  | 30 |  |  |  |  | DMZ | means valid data that systems were recovered from a real/fabricated fault. Data was labelled as 0.
|  | 833 | IED_FDR (FDR) | 4 | 8331a-8331d |  |  |  | 8331 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 831 | IED_XFMR1 (66kV) | 1 | 8312a | (8312, 8322, 8332) Inject 40 messages (500ms HB) to mislead associated CBs with fake closing signals |  | IED_PIOC_XFMR1 | 8312 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8312b | [5 empty] | 30 | 20 | 40 | 30 | 30 | 20 | 40 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8312c |  |  | IED_PIOC_XFMR2 | 8312 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8312d | [8 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8322a-8322b |  |  | IED_PIOC_FDR | 8322 |  |  |  |  | 30
|  | 833 | IED_FDR (FDR) | 4 | 8332a-8332d |  |  |  | 8332 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 831 | IED_XFMR1 (66kV) | 1 | 8313a | (8313, 8323, 8333) Inject messages with 1,4,16,64,256,1000ms HB to mislead associated CBs with fake closing signals |  | IED_PIOC_XFMR1 | 8313 |  | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8313b | [5 empty] | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8313c |  |  | IED_PIOC_XFMR2 | 8313 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8313d | [8 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8323a-8323b |  |  | IED_PIOC_FDR | 8323 |  |  |  |  | 30
|  | 833 | IED_FDR (FDR) | 4 | 8333a-8333d |  |  |  | 8333 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 831 | IED_XFMR1 (66kV) | 1 | 8314a | (8314, 8324, 8334) Inject 30 messages with 1,4,16,64,256,1000ms HB to mislead associated CBs with fake closing signals |  | IED_PIOC_XFMR1 | 8314 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8314b | [5 empty] | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8314c |  |  | IED_PIOC_XFMR2 | 8314 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8314d | [8 empty] | 30
|  | 832 | IED_FDR (22kV) | 2 | 8324a-8324b |  |  | IED_PIOC_FDR | 8324 |  |  |  |  | 30
|  | 833 | IED_FDR (FDR) | 4 | 8334a-8334d |  |  |  | 8334 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
| Alter | 841 | IED_XFMR1 (66kV) | 1 | 8411a | (8411, 8421, 8431) Alter all messages to mislead associated CBs with fake closing signals |  | IED_PIOC_XFMR1 | 8411 |  | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8411b | [5 empty] | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8411c |  |  | IED_PIOC_XFMR2 | 8411 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8411d | [8 empty] | 30
|  | 842 | IED_FDR (22kV) | 2 | 8421a-8421b |  |  | IED_PIOC_FDR | 8421 |  |  |  |  | 30
|  | 843 | IED_FDR (FDR) | 4 | 8431a-8431d |  |  |  | 8431 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 841 | IED_XFMR1 (66kV) | 1 | 8412a | (8412, 8422, 8432) Alter the first 30 messages to mislead associated CBs with fake closing signals |  | IED_PIOC_XFMR1 | 8412 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8412b | [5 empty] | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8412c |  |  | IED_PIOC_XFMR2 | 8412 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8412d | [8 empty] | 30
|  | 842 | IED_FDR (22kV) | 2 | 8422a-8422b |  |  | IED_PIOC_FDR | 8422 |  |  |  |  | 30
|  | 843 | IED_FDR (FDR) | 4 | 8432a-8432d |  |  |  | 8432 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
When short-circuit faults happen, mislead irrelevant CBs with fake opening signals to trigger unnecessary protection, and thus deteriorate the impacts of the short-circuit faults. | Add | 851 | IED_XFMR1 (66kV) | 1 | 8511a | (8511, 8521, 8531) Inject messages (500ms HB) to mislead other irrelevant CBs with fake opening signals until the associated CBs start to reset (the fault is eliminated and the systems recover). 66bus1-66bus2 (2), XFMR1-XFMR2 (2), 22bus1-22bus2 (2), FDR1-FDR2 (2), FDR3-FDR4 (2) |  | IED_PIOC_XFMR1 | 8511 |  | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8511b | [5 empty] | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8511c |  |  | IED_PIOC_XFMR2 | 8511 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8511d | [8 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8521a-8521b |  |  | IED_PIOC_FDR | 8521a-8521b |  |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8531a-8531d |  |  |  | 8531a-8531d |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 851 | IED_XFMR1 (66kV) | 1 | 8512a | (8512, 8522, 8532) Inject 40 messages (500ms HB) to mislead other irrelevant CBs with fake opening signals |  | IED_PIOC_XFMR1 | 8512 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8512b | [5 empty] | 30 | 20 | 40 | 30 | 30 | 20 | 40 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8512c |  |  | IED_PIOC_XFMR2 | 8512 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8512d | [8 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8522a-8522b |  |  | IED_PIOC_FDR | 8522a-8522b |  |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8532a-8532d |  |  |  | 8532a-8532d |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 851 | IED_XFMR1 (66kV) | 1 | 8513a | (8513, 8523, 8533) Inject messages with 1,4,16,64,256,1000ms HB to mislead other irrelevant CBs with fake opening signals until the associated CBs start to reset (the fault is eliminated and the systems recover). |  | IED_PIOC_XFMR1 | 8513 |  | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8513b | [5 empty] | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8513c |  |  | IED_PIOC_XFMR2 | 8513 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8513d | [8 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8523a-8523b |  |  | IED_PIOC_FDR | 8523a-8523b |  |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8533a-8533d |  |  |  | 8533a-8533d |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 851 | IED_XFMR1 (66kV) | 1 | 8514a | (8514, 8524, 8534) Inject 30 messages with 1,4,16,64,256,1000ms HB to mislead other irrelevant CBs with fake opening signals |  | IED_PIOC_XFMR1 | 8514 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8514b | [5 empty] | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8514c |  |  | IED_PIOC_XFMR2 | 8514 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8514d | [8 empty] | 30
|  | 852 | IED_FDR (22kV) | 2 | 8524a-8524b |  |  | IED_PIOC_FDR | 8524a-8524b |  |  |  |  | 30
|  | 853 | IED_FDR (FDR) | 4 | 8534a-8534d |  |  |  | 8534a-8534d |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
| Alter | 861 | IED_XFMR1 (66kV) | 1 | 8611a | (8611, 8621, 8631) when a short-circuit fault happens, an irrelevant IED (compromised with a malicious program) publishes packets containing tripping signals until the fault is eliminated and the systems recover. 66bus1-66bus2 (2), XFMR1-XFMR2 (2), 22bus1-22bus2 (2), FDR1-FDR2 (2), FDR3-FDR4 (2) |  | IED_PIOC_XFMR1 | 8611 |  | Fault-free | Emergency&Attacks |  | 30 | Fault-free | Emergency&Attacks |  | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8611b | [5 empty] | 30 | 60 |  | 30 | 30 | 60 |  | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8611c |  |  | IED_PIOC_XFMR2 | 8611 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8611d | [8 empty] | 30
|  | 862 | IED_FDR (22kV) | 2 | 8621a-8621b |  |  | IED_PIOC_FDR | 8621 |  |  |  |  | 30
|  | 863 | IED_FDR (FDR) | 4 | 8631a-8631d |  |  |  | 8631ab, 8631cd |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
|  | 861 | IED_XFMR1 (66kV) | 1 | 8612a | (8612, 8622, 8632) when a short-circuit fault happens, an irrelevant IED (compromised with a malicious program) publishes the first 30 packets containing tripping signals, and the rest packets containing non-tripping signals. |  | IED_PIOC_XFMR1 | 8612 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 8612b | [5 empty] | 30 | 25 | 35 | 30 | 30 | 25 | 35 | 210
|  |  | IED_XFMR2 (66kV) | 1 | 8612c |  |  | IED_PIOC_XFMR2 | 8612 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 8612d | [8 empty] | 30
|  | 862 | IED_FDR (22kV) | 2 | 8622a-8622b |  |  | IED_PIOC_FDR | 8622 |  |  |  |  | 30
|  | 863 | IED_FDR (FDR) | 4 | 8632a-8632d |  |  |  | 8632ab, 8632cd |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
Total Datasets (with labels) |  |  |  | 150 |  | Total malicious programs
When short-circuit faults happen, delete trip messages | Delete | 871 | IED_XFMR1 (66kV) | 1 | 871a | Delete the first 40 GOOSE trip packets when a fault occurs. Thus, delay protection for almost 35 seconds. |  | IED_PIOC_XFMR1 | 871 |  | Fault-free | Em&Attack | Emergency | 30 | Fault-free | Em&Attack | Emergency | Total
|  |  | IED_XFMR1 (XFMR) | 1 | 871b | [5 empty] | 30 | 35 | 55 | 30 | 30 | 35 | 25 | 240
|  |  | IED_XFMR2 (66kV) | 1 | 871c |  |  | IED_PIOC_XFMR2 | 871 |  |  |  |  | 30
|  |  | IED_XFMR2 (XFMR) | 1 | 871d | [8 empty] | 30
|  | 872 | IED_FDR (22kV) | 2 | 872a-872b |  |  | IED_PIOC_FDR | 872 |  |  |  |  | 30
|  | 873 | IED_FDR (FDR) | 4 | 873a-873d |  |  |  | 873 |  | 1st attack cycle |  |  | 30 | 2nd attack cycle (start from 120th)
Additional Datasets (without labels) |  |  |  | 10 |  | Additional malicious programs

## Benign-behaviour-only
Scenario type | Label | No. of datasets | Descriptions | Time sections of successive behaviours in seconds |  |  |  | Total
Fault-free | 0 | 1 | No unusual events happen. | All fault-free |  |  |  | 270
|  |  |  | Fault-free | Emergency | Fault-free (recovery) | Emergency
Emergency operation | 101 | 1 | When a short-circuit fault occurs on Fault_66bus1, open CB1_66KV, CB2_66KV and CB_XFMR1; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 102 | 1 | When a short-circuit fault occurs on Fault_66bus2, open CB2_66KV, CB3_66KV and CB_XFMR2; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 103 | 1 | When a short-circuit fault occurs on Fault_XFMR1, open CB1_66KV, CB2_66KV and CB_XFMR1; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 104 | 1 | When a short-circuit fault occurs on Fault_XFMR2, open CB2_66KV, CB3_66KV and CB_XFMR2; close CB2_22KV | 30 | 90 | 60 | 90 | 270
| 105 | 1 | When a short-circuit fault occurs on Fault_22bus1, open CB1_22KV | 30 | 90 | 60 | 90 | 270
| 106 | 1 | When a short-circuit fault occurs on Fault_22bus2, open CB3_22KV | 30 | 90 | 60 | 90 | 270
| 107 | 1 | When a short-circuit fault occurs on Fault_FDR1, open CB_FDR1 | 30 | 90 | 60 | 90 | 270
| 108 | 1 | When a short-circuit fault occurs on Fault_FDR2, open CB_FDR2 | 30 | 90 | 60 | 90 | 270
| 109 | 1 | When a short-circuit fault occurs on Fault_FDR3, open CB_FDR3 | 30 | 90 | 60 | 90 | 270
| 110 | 1 | When a short-circuit fault occurs on Fault_FDR4, open CB_FDR4 | 30 | 90 | 60 | 90 | 270